Battery Storage
Hydrogen Gas
Leak Detection

Hydrogen Gas Detection System

PART 1 – GENERAL

- RELATED DOCUMENTS

  - Drawings and general provisions of the Contract, including General and Supplementary General Conditions and other Division 01 Specification Sections, apply to this Section

PART 2 – PRODUCTS

  - Gas Detection System (S&S Middle East HGD100)

    - A wall-mountable hydrogen gas detector capable of monitoring hydrogen gas concentrations in battery storage facilities.

    - System shall have outputs for integration with building management systems (BAS) using Bacnet MS/TP or Modbus RTU communication protocols.

    - System shall have internal volt free relays, 0-10V and 4-20mA to activate ventilation equipment and warning alarms upon reaching alarm thresholds.

    - Wall-mounted at a height recommended by the manufacturer.

    - Alarm thresholds shall be 1% Warning (Pre-Alarm) 2% Alarm.

    - System shall include a 10 years life span with end of life indication.

    - System shall include a replaceable sensor module for extended product life.

    - System shall include a 4-second alarm delay to prevent false alarms caused by transient hydrogen levels.

    - System shall have the option for 230V, 24VAC or 18-60VDC powered.

    - System shall have an operating temperature range: -10°C to 40°C (14°F to 104°F).

    - Acceptable products: S&S Middle East HGD100

PART 3 – EXECUTION

  - INSTALLATION

    - Sensors must be installed in compliance with the manufacturer's guidelines.

    - Install wiring and conduit to prevent interference with other systems.

    - Ensure accessibility for future sensor maintenance and calibration.