Car Park CO & NO2 Gas Detection

Standalone Car Park Gas Detector

PART 1 – GENERAL

- RELATED DOCUMENTS

  - Drawings and general provisions of the Contract, including General and Supplementary General Conditions and other Division 01 Specification Sections, apply to this Section

PART 2 – PRODUCTS

  - Gas Detection System (S&S Middle East GM100-CO-NO2)

    - A wall-mountable combined carbon monoxide & nitrogen dioxide gas detector capable of monitoring CO & NO2 gas concentrations in enclosed car parking facilities.

    - System shall have outputs for integration with building management systems (BAS) using Bacnet MS/TP or Modbus RTU communication protocols.

    - System shall have internal volt free relays, 0-10V and 4-20mA to activate ventilation equipment and warning alarms upon reaching alarm thresholds.

    - Wall-mounted at a height recommended by the manufacturer.

    - Alarm thresholds shall be factory set at the following:

      - (CO) 25ppm low level, 100ppm high level

      - (NO2) 0.7ppm low level, 2ppm high level

    - System shall include a replaceable sensor module for extended product life.

    - System shall be 24VAC/DC powered.

    - System shall have an operating temperature range: -20°C to 50°C.

    - System shall have internal audible alarm built-in 85dB at 3m.

    - Acceptable products: S&S Middle East GM100-CO-NO2

PART 3 – EXECUTION

  - INSTALLATION

    - Sensors must be installed in compliance with the manufacturer's guidelines.

    - Install wiring and conduit to prevent interference with other systems.

    - Ensure accessibility for future sensor maintenance and calibration.