VRF 
Refrigerant Gas Detection

VRF Refrigerant Detection System

PART 1 – GENERAL

- RELATED DOCUMENTS

  - Drawings and general provisions of the Contract, including General and Supplementary General Conditions and other Division 01 Specification Sections, apply to this Section

  - SUMMARY

  - Provide a complete installation of refrigerant gas monitors as required in conditioned spaces as specified on plans, or in rooms that do not comply with ASHRAE 15 minimum room volume requirements.

  - The system shall include, but not be limited to, the following:

    - VRF refrigerant gas detector with local alarm and BMS communication.

  - SUBMITTALS

  - Provide data for each factory supplied piece of equipment including model numbers.

  - Shop Drawings

    - Wiring diagrams.

    - Schematic of system components and set up.

PART 2 – PRODUCTS

  - Detectors (S&S Middle East RS VRF SERIES)

    - BACnet MS/TP or Modbus RTU output for BMS integration is required, with readable and writable settings.

    - Up to 127 units per communication chain.

    - Appearance: Detector shall be no more than 86mm x 114mm x 25mm and must be designed for use in occupied spaces.

    - Visual indication: multicolor status LED indication.

    - Installation: 300mm from the floor.

    - Dry contact output and 0-10V linear output for additional communication and equipment control as needed.

    - Maximum system maintenance requirements: the detectors shall require no annual calibration, only an annual span check with a factory supplied gas concentration.

    - The detector shall utilize a non-dispersive infrared type (NDIR) with a minimum accuracy of +/- 5% FS range below 50% F.S. and +/- 7% of FS range above 50% full scale.

    - Detectors shall be of the diffusion type.

    - Power supply: 90-250VAC or 24V.

    - Factory set high alarm levels to the corresponding ASHRAE OEL value.

    - Pre-alarm levels shall be factory set to the specifications in this document.

    - The detectors shall be capable of sensing for the type of refrigerant specified in the equipment and shall come factory calibrated.

    - Integral audible alarm: 85dB @ 3m.

[Remove tables as necessary. All high alarm levels reflect ASHRAE OEL.]

| GAS | Pre Alarm (PPM) | High Alarm (PPM) | Mounting Height |
| --- | --- | --- | --- |
| R-1233zd | 75 | 1000 | 300mm A.F.F. |
| R-1234yf | 175 | 1000 | 300mm A.F.F. |
| R-1234ze | 175 | 1000 | 300mm A.F.F. |
| R-123 |  | 50 | 300mm A.F.F. |
| R-125 | 75 | 1000 | 300mm A.F.F. |
| R-134a | 175 | 1000 | 300mm A.F.F. |
| R-143a | 75 | 1000 | 300mm A.F.F. |
| R-227ea | 75 | 1000 | 300mm A.F.F. |
| R-22 | 75 | 1000 | 300mm A.F.F. |
| R-438a | 75 | 990 | 300mm A.F.F. |
| R-32 | 350 | 1000 | 300mm A.F.F. |
| R-404a | 175 | 1000 | 300mm A.F.F. |
| R-407a | 75 | 1000 | 300mm A.F.F. |
| R-407c | 175 | 1000 | 300mm A.F.F. |
| R-407f | 75 | 1000 | 300mm A.F.F. |
| R-410a | 350 | 1000 | 300mm A.F.F. |
| R-417a | 75 | 1000 | 300mm A.F.F. |
| R-422a | 75 | 1000 | 300mm A.F.F. |
| R-427a | 75 | 1000 | 300mm A.F.F. |
| R-434a | 75 | 1000 | 300mm A.F.F. |
| R-448a | 75 | 860 | 300mm A.F.F. |
| R-449a | 175 | 800 | 300mm A.F.F. |
| R-450a | 75 | 880 | 300mm A.F.F. |
| R-452a | 75 | 790 | 300mm A.F.F. |
| R-452b | 75 | 870 | 300mm A.F.F. |
| R-453a | 75 | 1000 | 300mm A.F.F. |
| R-454a | 75 | 690 | 300mm A.F.F. |
| R-454b | 75 | 850 | 300mm A.F.F. |
| R-454c | 75 | 620 | 300mm A.F.F. |
| R-455a | 75 | 650 | 300mm A.F.F. |
| R-507 | 75 | 1000 | 300mm A.F.F. |
| R-513a | 75 | 650 | 300mm A.F.F. |
| R-514a | 75 | 320 | 300mm A.F.F. |
| R-442a | 75 | 1000 | 300mm A.F.F. |
| R-422d | 75 | 1000 | 300mm A.F.F. |
| R-424a | 75 | 990 | 300mm A.F.F. |

PART 3 – EXECUTION

  - INSTALLATION

    - Comply with ASHRAE 15.

    - Install hazardous gas monitoring equipment as shown on Contract Drawings, and as recommended by manufacturer of equipment, and as required by authorities having jurisdiction.

    - All sensors shall be mounting to the proper height in accordance with the manufacturer’s installation instructions.

    - Verify the refrigerant type being utilized and provide the proper refrigerant sensor from the manufacturer as required.

  - SEQUENCE OF OPERATION

    - Immediately upon pre-alarm level detection.

      - System status and gas concentration to be communication via BACnet MS/TP or Modbus RTU.

      - The detector LED displays amber.

    - Immediately upon high alarm level detection.

      - System status and gas concentrations to be communicated via BACnet MS/TP or Modbus RTU.

      - The detector LED displays red.

      - Internal buzzer sounds.