Water Leak
Detection System

Water Leak Monitoring

PART 1 – GENERAL

- RELATED DOCUMENTS

  - Drawings and general provisions of the Contract, including General and Supplementary General Conditions and other Division 01 Specification Sections, apply to this Section

  - The system shall include, but not limited to the following:

    - Future expandability

    - Central control and monitoring panel

    - LED system status indicator

    - BMS/BAS relay

    - In-built audible and visual alarms

    - Output for remote audible & visual alarm strobes

    - Manual re-set after alarm condition

    - Mute functions

- PRODUCTS

  - Water Leak Monitor (S&S Middle East WLM)

    - 24V or 230VAC Powered

    - LED Indication of Status

      - Alarm Status

      - Water On Status

    - Outputs Must Meet or Exceed Specs as Listed Below

    - BMS Relay Output

      - NC/COM/NO, max 3A @ 230V

    - Strobe Relay Output

      - NC/COM/NO, max 3A @ 230V

    - Local activation of audible and visual alarms of 60 dBa @ 1m

    - Manual reset function to clear any alarm conditions

    - Sensitivity adjustment of sensing attachments

    - Mute reset function to clear any alarm conditions

    - Acceptable products: S&S Middle East WLM

Delete below water leak sensor options as required.

  - Water Leak Sensing Cable (S&S Middle East WLMC 2 Core)

    - Pre-defined lengths as stated by the manufacturer.

    - Cable must be a quick drying type for re-use after water leak detection.

    - Must include a 2m lead cable as a minimum.

    - Manufacturer must have the option to include 4 core cable for fault detection, indicating faulty cables or incorrect wiring.

    - Acceptable products: S&S Middle East WLMC

  - Water Leak Sensing Cable (S&S Middle East WLMFC 4 Core)

    - Pluggable ropes with male and female plug ends for expandability and adaptability.

    - Tee attachments for multiple branches from one controller.

    - Cable must be a quick drying type for re-use after water leak detection.

    - Must include a 2m lead cable as a minimum.

    - Acceptable products: S&S Middle East WLMFC

  - Water Leak Puck Type (S&S Middle East WLMP)

    - Must be able to connect to 8 pucks to the main water leak detection controller.

    - Lead wire may be extended up to 30m.

    - Must be ABS material.

    - Acceptable products: S&S Middle East WLMP

PART 3 – EXECUTION

  - INSTALLATION

    - Sensors must be installed in compliance with the manufacturer's guidelines.

    - Install wiring and conduit to prevent interference with other systems.

    - Ensure accessibility for future sensor maintenance and calibration.